## Example Darcy
DARCY FRICTION LOSS CALCULATOR FOR PIPES, FITTINGS & VALVES
Given Data
| Flow Rate (Q) | m3/hr | 300 | 0.083333 | m3/s |  |  | INPUTS
| Pipe Inside Diameter (D) | mm | 203.1 | 0.2031 | m |  |  | CALCULATED VALUES
| Kinematic Viscosity (ν) | cSt | 100 | 0.0001 | m2/s
| Specific Roughness (Є) | m | 1.5e-06
| Pipe Length (L) | m | 74.5 |  |  |  | Specific Roughness Data
[7 empty] | Plastic |  | 1.5 | microns
| Calculated Data | [5 empty] | Steel |  | 45 | microns
| Average Velocity - V (m/s) |  | 2.5722 |  |  |  | Fibreglass (Generic) |  | 30 | microns
| Reynolds Number |  | 5224.1898 |  |  |  | Flowtite GRP |  | 29 | microns
| Darcy Friction Factor |  | 0.037356
| Head Loss - Pipe (m) |  | 4.6209 |  |  | TOTAL HEAD LOSS, hf (m) | 9.7467
Calculated Head Loss in Fittings, Valves, Entrances & Exits
|  |  | K | Qty | Sub Total K
| Angle Valve |  | 5 | 0 | 0
| Ball Valve, Full Port |  | 0.05 | 0 | 0
| Butterfly Valve |  | 0.6 | 0 | 0
| Check Valve, Swing Type |  | 2.3 | 1 | 2.3
| Elbow 45 Degrees |  | 0.4 | 0 | 0
| Elbow 90 Degrees, Long Radius |  | 0.6 | 0 | 0
| Elbow 90 Degrees, Standard |  | 0.9 | 3 | 2.7
| Flow Meter, Turbine Type |  | 7 | 0 | 0
| Foot Valve |  | 0.9 | 0 | 0
| Gate Valve |  | 0.2 | 1 | 0.2
| Globe Valve |  | 10 | 1 | 10
| Pipe Entrance, Inward Projected Pipe |  | 1 | 0 | 0
| Pipe Entrance, Sharp Edge |  | 0.5 | 0 | 0
| Pipe Exit |  | 1 | 0 | 0
| Tee, Standard, Flow Through Branch |  | 1.8 | 0 | 0
| Tee, Standard, Flow Through Run |  | 0.6 | 0 | 0
15.2
| Head Loss - Valves & Fittings (m) |  | 5.1258

## Example HLA
DARCY FRICTION LOSS CALCULATOR FOR PIPES, FITTINGS & VALVES
Given Data
| Flow Rate (Q) | m3/hr | 3000 | 0.83333 | m3/s |  |  | INPUTS
| Pipe Inside Diameter (D) | mm | 500 | 0.5 | m |  |  | CALCULATED VALUES
| Kinematic Viscosity (ν) | cSt | 1 | 1e-06 | m2/s
| Specific Roughness (Є) | m | 3e-05
| Pipe Length (L) | m | 120 |  |  |  | Specific Roughness Data
[7 empty] | Plastic |  | 1.5 | microns
| Calculated Data | [5 empty] | Steel |  | 45 | microns
| Average Velocity - V (m/s) |  | 4.2441 |  |  |  | Fibreglass (Generic) |  | 30 | microns
| Reynolds Number |  | 2122065.9079 |  |  |  | Flowtite GRP |  | 29 | microns
| Darcy Friction Factor |  | 0.012046
| Head Loss - Pipe (m) |  | 2.6543 |  |  | TOTAL HEAD LOSS, hf (m) | 3.756
Calculated Head Loss in Fittings, Valves, Entrances & Exits
|  |  | K | Qty | Sub Total K
| Angle Valve |  | 5 | 0 | 0
| Ball Valve, Full Port |  | 0.05 | 0 | 0
| Butterfly Valve |  | 0.6 | 1 | 0.6
| Check Valve, Swing Type |  | 2.3 | 0 | 0
| Elbow 45 Degrees |  | 0.4 | 1 | 0.4
| Elbow 90 Degrees, Long Radius |  | 0.6 | 0 | 0
| Elbow 90 Degrees, Standard |  | 0.9 | 0 | 0
| Flow Meter, Turbine Type |  | 7 | 0 | 0
| Foot Valve |  | 0.9 | 0 | 0
| Gate Valve |  | 0.2 | 1 | 0.2
| Globe Valve |  | 10 | 0 | 0
| Pipe Entrance, Inward Projected Pipe |  | 1 | 0 | 0
| Pipe Entrance, Sharp Edge |  | 0.5 | 0 | 0
| Pipe Exit |  | 1 | 0 | 0
| Tee, Standard, Flow Through Branch |  | 1.8 | 0 | 0
| Tee, Standard, Flow Through Run |  | 0.6 | 0 | 0
1.2
| Head Loss - Valves & Fittings (m) |  | 1.1017