## Darcy Newtonian
DARCY FRICTION LOSS CALCULATOR FOR PIPES, FITTINGS & VALVES
Given Data
| Flow Rate (Q) | m3/hr | 576 | 0.16 | m3/s |  |  | INPUTS
| Pipe Inside Diameter (D) | mm | 277.1 | 0.2771 | m |  |  | CALCULATED VALUES
| Kinematic Viscosity (ν) | cSt | 21.429 | 2.1429e-05 | m2/s
| Specific Roughness (Є) | m | 1.5e-06
| Pipe Length (L) | m | 100 |  |  |  | Specific Roughness Data
[7 empty] | Plastic |  | 1.5 | microns
| Calculated Data | [5 empty] | Steel |  | 45 | microns
| Average Velocity - V (m/s) |  | 2.6531 |  |  |  | Fibreglass |  | 29 | microns
| Reynolds Number |  | 34307.7053
| Darcy Friction Factor |  | 0.022659
| Head Loss - Pipe (m) |  | 2.9337 |  |  | TOTAL HEAD LOSS, hf (m) | 2.9337
Calculated Head Loss in Fittings, Valves, Entrances & Exits
|  |  | K | Qty | Sub Total K
| Angle Valve |  | 5 | 0 | 0
| Ball Valve, Full Port |  | 0.05 | 0 | 0
| Butterfly Valve |  | 0.6 | 0 | 0
| Check Valve, Swing Type |  | 2.3 | 0 | 0
| Elbow 45 Degrees |  | 0.4 | 0 | 0
| Elbow 90 Degrees, Long Radius |  | 0.6 | 0 | 0
| Elbow 90 Degrees, Standard |  | 0.9 | 0 | 0
| Flow Meter, Turbine Type |  | 7 | 0 | 0
| Foot Valve |  | 0.9 | 0 | 0
| Gate Valve |  | 0.2 | 0 | 0
| Globe Valve |  | 10 | 0 | 0
| Pipe Entrance, Inward Projected Pipe |  | 1 | 0 | 0
| Pipe Entrance, Sharp Edge |  | 0.5 | 0 | 0
| Pipe Exit |  | 1 | 0 | 0
| Tee, Standard, Flow Through Branch |  | 1.8 | 0 | 0
| Tee, Standard, Flow Through Run |  | 0.6 | 0 | 0
0
| Head Loss - Valves & Fittings (m) |  | 0

## Darby Bingham
DARBY METHOD FOR DETERMINING HEAD LOSS FOR BINGHAM PLASTIC SLURRIES
Given Data
| Flow Rate (Q) | m3/hr | 576 | 0.16 | m3/sec | INPUTS
| Pipe Inside Diameter (D) | mm | 277.1 | 0.2771 | metres | CALCULATED VALUES
| Bingham Yield Stress (τYB) | Pa | 20
| Plastic Viscosity (ηP) | mPa.s | 30 | 0.03 | Pa.s
| Pipe Length (L) | m | 100
| Slurry Density (ρ) | kg/m3 | 1400
Calculated Data
| Average Velocity (V ) | m/s | 2.6531
| Bingham Reynolds Number (RBP) | - | 34308.3914
| Hedstrom Number (He) | - | 2388848.3111
| m | - | 2.8659
| a | - | -1.47
| b | - | -0.193
| Turbulent Friction Factor (ffT) | - | 0.0045151
| Laminar Friction Factor (ffL) | - | 0.0058783
| Combined Fanning Friction Factor (ff) | - | 0.0067233
| Head Loss in Straight Pipe (hf) | m | 3.4819 | metres of slurry
| Pressure Drop per metre (ΔP/L) | Pa/m | 478.2091
| Wall Shear Stress (τw) | Pa | 33.1279

## Irvine Power Law
IRVINE METHOD FOR DETERMINING HEAD LOSS FOR POWER LAW SLURRIES
Given Data
| Flow Rate (Q) | m3/hr | 1080 | 0.3 | m3/s | INPUTS
| Pipe Inside Diameter (D) | mm | 300 | 0.3 | m | CALCULATED VALUES
| Power Law Consistency Coefficient (K) | Pa.sn | 2.74
| Power Law Behaviour Index (n) | - | 0.3
| Pipe Length (L) | m | 50
| Slurry Density (ρ) | kg/m3 | 1000
Calculated Data
| Average Velocity (V ) | m/s | 4.2441
| Metzner Reed Reynolds Number (RMR) | - | 12728.8706
| D(n) | - | 0.29231
| Fanning Friction Factor (ff) | - | 0.0036178
| Head Loss in Straight Pipe (hf) | m | 2.2143
| Pressure Drop per metre (ΔP/L) | Pa/m | 434.4433
| Wall Shear Stress (τw) | Pa | 32.5833

## Slatter Herschel Transition
SLATTER METHOD FOR DETERMINING THE TRANSITION FROM LAMINAR TO TURBULENT FLOW
FOR ALL SLURRIES
| Given Data |  |  |  |  | GUESS INPUT
| Flow Rate (Q) | m3/hr | 540 | 0.15 | m3/sec | INPUTS
| Pipe Inside Diameter (D) | mm | 200 | 0.2 | metres | CALCULATED VALUES
| Herschel-Bulkley Yield Stress (τYH) | Pa | 6
| K | mPa.s | 30 | 0.03 | Pa.s
| n | - | 0.9
| Slurry Density (ρ) | kg/m3 | 1150
| Wall Shear Stress (τw) | Pa | 9.95 | Goal Seek Cells
Calculated Data
| Average Velocity (V ) | m/s | 4.7746
| ϕ | - | 0.60302
| Transitional Volumetric Flow Rate (Q) | m3/s | 0.076694
| Plug Radius (Rp) | m | 0.060302
| Plug Velocity (Vplug) | m/s | 4.2583
| Plug Flow Rate (Qplug) | m3/s | 0.048645
| Annulus Flow Rate (Qann) | m3/s | 0.028048
| Velocity in Sheared Annulus (Vann) | m/s | 1.403
| Equivalent Diameter of Sheared Region (Dshear) | m | 0.079397
| Slatter Modified Reynolds Number (Rmod) | - | 2109.3708 | 2100 | Rmod @ Transition Point
| Velocity at the Transition Point (VHB-TR) | m/s | 2.4412
Notes:
For Bingham Plastic slurries, set n=1, τYB = τYB and ηP = K